GENERAL SPECIFICATIONS FOR PORT-A-CABIN HOUSING UNITS

1. General:

Single wide portable buildings will be 40x12 ft. (12.2 meters x 3.7 meter) with 8.5’ (2.5

meter) interior height. Unique trailers will be built to the size in the drawings and will

conform to all other specifications in this statement of work. All trailers and the materials

used in the trailer will be new and built to U.S. Standard.

2. Steel Frame & Structure are designed as per standard specification:

Heavy-duty 2 main runners, end rails and cross members, (Ref. Our Drawing) Built out of 14cm C-channel, 12cm I-beam with 5 cm x 5cm hollow sections.

All steel beams are coated with Red-oxide primer (cleaned and painted in a corrosive

resistant paint). Provided with minimum of 4 crane Lifting Points.

3. Wall Interior & Exterior:

75mm thick Sandwich-Panel less corrugated pre-painted steel sheets.

4. Wood trim the same color of the paneling will cover the gaps between the

paneling:

Wet trailer Walls will have a vapor barrier and be covered with 3/8” Marine Grade

Plywood covered by waterproof polyurethane sheeting with watertight trim in the gaps

(polyurethane sandwich panel).

5. Insulation:

Minimum of 75mm of Polyurethane (wet and dry) at minimum R12.

6. Floor:

18mm Plywood fixed on steel and steel joists, covered with carpet or 1.5mm thick PVC-

Vinyl tiles.

All Sub flooring for wet trailers will be a minimum of ¾” Marine Grade Plywood Grade B-B and covered with 3mm sheet linoleum / vinyl.

7. Roof:

- Finish - .047” (2mm) PVC fully adhered membrane roofing (white).

- Sheathing - 15/32”(13mm) exterior sheathing

- Slope - Structural wood rafters cut for slope. (Min 2 X4) (5cm x 10cm)

- Joists and Plates - 2”x4” (5cm x 10cm) @ 16” (41cm) on center.

- Insulation - 10cm fiberglass with a commercial grade vapor barrier. (R-20)

- Ceiling Finish - White vinyl covered plywood (4mm)

- Trim -vinyl covered matching divider molding

The interior roof of the roof with be 3/8” Marine Grade Plywood covered by water proof

polyurethane sheeting with watertight trim in the gaps.

8. Doors:

Lockable metal (aluminum heavy-duty) doors (exterior) will be provided. The door frame

in addition to allowing the door to lock effectively will have a rubber or similar weather

striping barrier that will keep out wind, sand and other airborne elements and allow for

efficient cooling and heating of the space. Doors shall lock by key set and have a

deadbolt. With a minimum of 3 keys per door delivered at the time of delivery. Door will

be Equipped with automatic door closer. Keep the door fully open position.

Interior doors will be wooden finish.

9. Windows:

Silver anodized aluminum frame (Non thermal break), horizontal sliding window (one

fixed, one sliding) with insect screen and weather stripping, 6mm thick clear glass (Single glazing), overall size 800mm x 1000mm . Venetian blinds shall be provided for all windows.

10. Air conditioner / HVAC:

24000 BTU, 240 Volts, 50Hz Heat & Cold Air-condition will be installed. (This will keep the interior at 70 degrees Fahrenheit/20 degrees celcious.units will be either UL© or CE© approved.)

11. Plumbing:

All plumbing materials used will be UL© or CE© certified to include pipes, pipe adhesive and plumbing fixtures.

Cold and Hot water service will be clearly marked at the valves. Blue coloring for cold

water and red coloring for hot water.

A 20 gallon / 80 liter water heater will be used in the bathrooms and be connected to the

shower and bathroom sink.

Exhaust fans will provided in each bathroom.

A drainage hole of at least 1” in diameter hooked to the grey water line will be placed

flush with or recessed into the floor to allow for spilled water to effectively be removed

from the bathroom area..

All fixtures will have non-flexible traps (p-traps) that will keep odors from the black/gray

water line from coming up through the lines a entering the facility.

A shower enclosure will be provided on the shower-tray for in order to prevent extra water from flowing into the entire bathroom area. All plumbing fixtures will be as per client's requirement.

12. Steps:

Steel (Galvanized and painted) steps will be provided. Steps shall be physically attached

to the trailer at each doorway. The step height shall be between 4 and 7 inches (10 and

18 cm) and the tread depth shall be 11 inches (28 cm). The angle of the stairs shall be

between 30 and 50 degrees.

13. Fire Extinguishers:

Minimum of 3 kg 2-A: 10-B: C dry chemical fire extinguishers, wall mounted by each

exit/entrance door on all portable building designs. These extinguishers will be new and

fully charged and certified prior to delivery. Extinguishers will be located on the interior

wall near each exit door at approximately 1 meter off of the ground in a bracket approved

by the extinguisher manufacture.

The ABC extinguisher will be either UL© or British Standard Institute approved.

14. Smoke / CO detectors:

Battery operated (standard size AA or 9 Volt) back up capability, ceiling mounted smoke

detectors with a test feature will be provided. Detectors shall be installed in each

occupied room. This will be either CE/UL approved.

15. Electrical:

Electrical supply is 240V, 50 Hz as per requirement.

Electrical distribution board will be provided with ELCB incomer and MCB outgoing. (In accordance with NEC or equivalent)

We will test all electrical equipment including unit distribution panel, lighting fixtures, wall systems, receptacles and similar items.

Unit service entrances will be conduit stub downs through the floor for site connection.

Unit distribution panels will be complete with branch circuit breakers as required. Copper

Romex (or equivalent), cable to all devices and fixtures. If any wires are exposed in the

trailer, they will be covered with a conduit pipe or equivalent. All exterior lighting will be

weatherproof There will be no exposed wiring, and all splices will be in boxes with covers.

No aluminum wiring will be used, all wiring will be copper. All wiring will be IAW US code

All wiring products to include telephone and Internet CAT 5 cable will be IAW established US standard.

The lights are distributed as shown in the technical drawings and will be a 2 bulb

overhead 60W fluorescent or recessed type light fighting with 2 energy-saving lamps

inside. The switches for these lights should be located near the entrance/exit door to the

trailer and are located next to the switch for the external light. Also refer electrical design

drawings for more details.

Each door for entering or exiting the trailer must have at least a 40 Watt Bulb that is in a

weather resistant covering that has an On/Off switch on the interior of the trailer within 1

foot (30 cm) of the door. This switch will be collocated with the switch for the interior lighting.

16. Emergency Light Fixture:

Emergency light fixture with self-contained nickel cadmium battery pack to operate on

stand-by circuit for 90-minute (min.) operation will be provided. Unit will have test/re-set

and lamp failure indication buttons. Primary operating voltage shall be 240 volts.

Light switches, single way, double pole, weather proof, recessed mounted.

Conduits: PVC Conduits, well recessed.

Exhaust fan will be controlled by a switch.

Telephone out let will be CAT 5 (GREAY COLOR)

Data outlet will be CAT 5 (BLUE COLOR).